## Sheet1
List ID | Value数值 | List ID | Value数值 | Display显示 | Description说明
LFT上一次故障 | 0 | LFT上一次故障 | 0 | [No Error] (NOF)无故障 | No error detected没有检测到故障
| 2 |  | 2 | [EEPROM Control] (EEF1)内存控制卡故障 | EEPROM control内存控制卡故障
| 3 |  | 3 | [Incorrect Configuration] (CFF)不准确配置 | Incorrect configuration选装卡被更换或拆卸。 控制卡被更换为另一块不匹配的控制卡。 当前配置矛盾。
| 4 |  | 4 | [Invalid Configuration] (CFI)无效配置 | Invalid configuration无效配置
| 5 |  | 5 | [Modbus Com Interruption] (SLF1)Modbus 通信中断 | Modbus communication interruption Modbus 通信中断
| 6 |  | 6 | [Internal Link Error] (ILF)内部连接错误 | Internal communication interruption with option module 选件模块和变频器之间的通信中断
| 7 |  | 7 | [Fieldbus Com Interrupt] (CNF)现场总线通信中断 | Fieldbus communication interruption 现场总线通信中断
| 8 |  | 8 | [External Error] (EPF1)外部错误 | External detected error 外部检测到错误
| 9 |  | 9 | [Overcurrent] (OCF)过电流 | Overcurrent 过电流
| 10 |  | 10 | [Precharge Capacitor] (CRF1) 预充电故障 | Precharge capacitor 预充电故障
| 11 |  | 13 | [AI2 4-20mA loss] (LFF2) AI2 4-20mA信号丢失 | AI2 4-20mA loss AI2 4-20mA信号丢失
| 12 |  | 15 | [Input Overheating] (IHF)输入过热 | Input Overheating输入过热
| 15 |  | 16 | [Drive Overheating] (OHF)变频器过热 | Drive overheating变频器过热
| 16 |  | 17 | [Motor Overload] (OLF)电机过载 | Motor overload电机过载
| 17 |  | 18 | [DC Bus Overvoltage] (OBF)直流母线过压 | DC bus overvoltage直流母线过压
| 18 |  | 19 | [Supply Mains Overvoltage] (OSF)供电电源过电压 | Supply mains overvoltage 供电电源过电压
| 19 |  | 20 | [Single output phase loss] (OPF1)单相输出缺失] | Single output phase loss单相输出缺失]
| 20 |  | 21 | [Input phase loss] (PHF)输入电压缺相 | Input phase loss输入电压缺相
| 21 |  | 22 | [Supply Mains UnderV] (USF)供电电源欠压 | Supply mains undervoltage供电电源欠压
| 22 |  | 23 | [Motor short circuit] (SCF1)电机短路 | Motor short circuit电机短路
| 23 |  | 24 | [Motor Overspeed] (SOF)电机过速 | Motor overspeed电机过速
| 24 |  | 25 | [Autotuning Error] (TNF)自整定错误 | Autotuning detected error自整定错误
| 25 |  | 26 | [Internal Error 1] (INF1)内部错误1 | Internal error 1 (Rating)内部错误1
| 26 |  | 27 | [Internal Error 2] (INF2)内部错误2 | Internal error 2 (Soft)内部错误2
| 27 |  | 28 | [Internal Error 3] (INF3)内部错误3 | Internal error 3 (Intern Comm)内部错误3（内部通信）
| 28 |  | 29 | [Internal Error 4] (INF4)内部错误4 | Internal error 4 (Manufacturing)内部错误4
| 29 |  | 30 | [EEPROM Power] (EEF2)内部电源卡故障 | EEPROM power内部电源卡故障
| 30 |  | 32 | [Ground Short Circuit] (SCF3)接地短路 | Ground short circuit接地短路
| 32 |  | 33 | [Output Phase Loss] (OPF2)输出缺相 | Output phase loss输出缺相
| 33 |  | 34 | [CANopen Com Interrupt] (COF)CANopen通信中断 | CANopen communication interruptionCANopen通信中断
| 34 |  | 37 | [Internal Error 7] (INF7) 内部错误7 | Internal error 7 (Init) 内部错误7(CPLD通讯故障 )
| 35 |  | 38 | [Fieldbus Error] (EPF2) 现场总线错误 | External error detected by Fieldbus 现场总线错误
| 37 |  | 40 | [Internal Error 8] (INF8) 内部错误8 | Internal error 8 (Switching Supply) 内部错误8(内部电源故障)
| 38 |  | 42 | [PC Com Interruption] (SLF2) PC通信故障 | PC communication interruption PC通信故障
| 40 |  | 45 | [HMI Com Interruption] (SLF3) 图形显示终端通信中断 | HMI communication interruption 图形显示终端通信中断
| 41 |  | 51 | [Internal Error 9] (INF9) 内部错误9 | Internal error 9 (Measure) 内部电流测量电路出现故障
| 42 |  | 52 | [Internal Error 10] (INFA) 内部错误10 | Internal error 10 (Mains) 内部错误10(用户供电错误)
| 43 |  | 53 | [Internal Error 11] (INFB) 内部错误11 | Internal error 11 (Temperature) 内部错误11(热传感器出错)
| 44 |  | 54 | [IGBT Overheating] (TJF) IGBT过热 | IGBT overheating IGBT过热
| 45 |  | 55 | [IGBT Short Circuit] (SCF4) IGBT短路 | IGBT short circuit IGBT短路
| 51 |  | 56 | [Motor Short Circuit] (SCF5) 电机短路 | Motor short circuit 电机短路
| 52 |  | 60 | [Internal Error 12] (INFC) 内部错误12 | Internal error 12 (Internal current supply) 内部错误12(内部电流源错误)
| 53 |  | 64 | [Input Contactor] (LCF) 线路接触器错误 | input contactor 线路接触器错误
| 54 |  | 68 | [Internal Error 6] (INF6) 内部错误6 | Internal error 6 (Option) 内部错误6(不可识别或不兼容的选件板)
| 55 |  | 69 | [Internal Error 14] (INFE) 内部错误14 | Internal error 14 (CPU) 内部错误14(内部CPU错误)
| 56 |  | 71 | [AI3 4-20mA loss] (LFF3) AI3 4-20mA信号丢失 | AI3 4-20mA loss AI3 4-20mA信号丢失
| 57 |  | 72 | [AI4 4-20mA loss] (LFF4) AI4 4-20mA信号丢失 | AI4 4-20mA loss AI4 4-20mA信号丢失
| 58 |  | 73 | [Boards Compatibility] (HCF) 板件兼容性（配对）错误 | Boards compatibility 板件兼容性（配对）错误
| 59 |  | 77 | [Conf Transfer Error] (CFI2) 配置传输错误 | Configuration transfer error 配置传输错误
| 60 |  | 79 | [AI5 4-20 mA loss] (LFF5) AI5 4-20 mA 信号丢失 | AI5 4-20 mA loss AI5 4-20 mA 信号丢失
| 62 |  | 99 | [Channel Switch Error] (CSF) 通道切换错误 | Channel switching detected error 通道切换错误
| 64 |  | 100 | [Process Underload] (ULF) 欠载过程 | Process Underload 欠载过程错误
| 65 |  | 101 | [Process Overload] (OLC) 过载过程 | Process overload 过载过程错误
| 68 |  | 105 | [Angle error] (ASF) 角度误差 | Angle error 角度误差
| 69 |  | 106 | [AI1 4-20 mA loss] (LFF1) AI1 4-20 mA 信号丢失 | AI1 4-20 mA loss AI1 4-20 mA 信号丢失
| 70 |  | 107 | [Safety Function Error] (SAFF) 安全功能错误 | Safety function detected error 安全功能检测错误
| 71 |  | 110 | [AI2 Th Level Error] (TH2F) AI2 热故障阈值 | AI2 thermal level error AI2 热故障阈值
| 72 |  | 111 | [AI2 Thermal Sensor Error] (T2CF) AI2 热传感器错误 | Thermal sensor error on AI2 AI2 热传感器错误
| 73 |  | 112 | [AI3 Th Level Error] (TH3F) AI3 的热故障阈值 | AI3 thermal level error AI3 的热故障阈值
| 76 |  | 113 | [AI3 Thermal Sensor Error] (T3CF) AI3 热传感器错误 | Thermal sensor error on AI3 AI3 热传感器错误
| 77 |  | 114 | [PumpCycle start Error ] (PCPF) 泵循环启动错误 | Pump cycle start error 泵循环启动错误
| 79 |  | 115 | [Out Pressure Low] (OPLF) 出口压力低] | Outlet Pressure Low 出口压力低]
| 99 |  | 116 | [High Flow Error] (HFPF) 高流量错误 | High Flow error 高流量错误
| 100 |  | 117 | [Inlet Pressure Error] (IPPF) 入口压力错误] | Inlet Pressure detected error 入口压力错误]
| 101 |  | 119 | [Pump Low Flow Error] (PLFF) 泵低流量错误 | Pump low flow detected error 泵低流量错误
| 105 |  | 120 | [AI4 Th Level Error] (TH4F) AI4 热故障阈值 | AI4 thermal level error AI4 热故障阈值
| 106 |  | 121 | [AI4 Thermal Sensor Error] (T4CF) AI4 热传感器错误 | Thermal sensor error on AI4 AI4 热传感器错误
| 107 |  | 122 | [AI5 Th Level Error] (TH5F) AI5 热故障阈值 | AI5 thermal level error AI5 热故障阈值
| 112 |  | 123 | [AI5 Thermal Sensor Error] (T5CF) AI5 热传感器错误 | Thermal sensor error on AI5 AI5 热传感器错误
| 113 |  | 124 | [Anti Jam Error] (JAMF) 防堵塞错误 | Anti Jam detected error 防堵塞错误
| 114 |  | 125 | [Out Pressure High] (OPHF) 出口压力高 | Outlet Pressure High 出口压力高
| 120 |  | 126 | [Dry Run Error] (DRYF) 空运行错误 | Dry run detected error 空运行错误
| 121 |  | 127 | [PID Feedback Error] (PFMF) PID 反馈错误 | PID feedback detected error PID 反馈检测出错误
| 122 |  | 128 | [Program Loading Error] (PGLF) 程序加载错误 | Program loading detected error 程序加载错误
| 123 |  | 129 | [Program Running Error] (PGRF) 程序运行错误 | Program running detected error 程序运行检测到错误
| 127 |  | 130 | [Lead Pump Error] (MPLF) 主泵错误 | Lead pump not available 主泵错误
| 128 |  | 131 | [Low Level Error] (LCLF) 液位低故障 | Low Level error 液位低故障
| 129 |  | 132 | [High Level Error] (LCHF) 高液位故障 | High Level error 高液位故障
| 142 |  | 142 | [Internal Error 16] (INFG) 内部错误 16 | Internal error 16 (IO module - relay) 内部错误 16(继电器IO扩展模块出现内部错误)
| 143 |  | 143 | [Internal Error 17] (INFH) 内部错误 17 | Internal error 17 (IO module - Standard) 内部错误 17(串行存储器闪存格式错误)
| 144 |  | 144 | [Internal Error 0] (INF0) 内部错误 0 | Internal error 0 (IPC) 内部错误 0(控制板的微处理器之间的通信中断)
| 146 |  | 146 | [Internal Error 13] (INFD) 内部错误13 | Internal error 13 (Diff current) 内部错误13(差动电流偏离错误)
| 148 |  | 148 | [Motor Stall Error] (STF) 电机堵转错误 | Motor stall detected error 电机堵转错误
| 149 |  | 149 | [Internal Error 21] (INFL) 内部错误 21 | Internal error 21 (RTC) 内部错误 21(内部实时时钟错误)
| 150 |  | 150 | [Embd Eth Com Interrupt] (ETHF) 内嵌式以太网通讯中断 | Embedded Ethernet communication interruption 内嵌式以太网通讯中断
| 151 |  | 151 | [Internal Error 15] (INFF) 内部错误 15 | Internal error 15 (Flash) 内部错误 15(闪存格式错误)
| 152 |  | 152 | [Firmware Update Error] (FWER) 固件升级故障 | Firmware Update error 固件升级故障
| 153 |  | 153 | [Internal Error 22] (INFM) 内部错误 22 | Internal error 22 (Embedded Ethernet) 内部错误 22(嵌入式以太网适配器错误)
| 154 |  | 154 | [Internal Error 25] (INFP) 内部错误 25 | Internal error 25 (Incompatibility CB & SW) 内部错误 25(控制板硬件版本与固件版本之间的不兼容性)
| 155 |  | 155 | [Internal Error 20] (INFK) 内部故障 20 | Internal error 20 (option interface PCBA) 内部故障 20(选件模块接口板错误)
| 156 |  | 157 | [Internal Error 19] (INFJ) 内部故障 19 | Internal error 19 (Encoder module) 内部故障 19(检测到了编码器模块错误)
| 157 |  | 158 | [Internal Error 27] (INFR) 内部错误 27 | Internal error 27 (Diagnostics CPLD) 内部错误 27(CPLD 中的诊断功能已检测到错误)
| 158 |  | 159 | [Internal Error 23] (INFN) 内部错误 23 | Internal error 23 (Module link) 内部错误 23(模块连接)
| 159 |  | 160 | [AFE ShortCircuit error] (SCF6) AFE 短路故障 | AFE ShortCircuit error AFE 短路故障
| 160 |  | 161 | [AFE Bus unbalancing ] (OBF2) AFE 母线不平衡 | AFE Bus unbalancing AFE 母线不平衡
| 161 |  | 173 | [Internal Error 28] (INFS) 内部错误 28 | Internal error 28 (AFE) 内部错误 28(AFE)
| 162 |  | 174 | [AFE Mains Undervoltage ] (URF) AFE 主电源欠压 | AFE Mains undervoltage AFE 主电源欠压
| 163 |  | 175 | [Internal Error 31] (INFV) 内部错误 31 | Internal error 31 (Missing brick) 内部错误 31(拓扑错误)
| 164 |  | 176 | [Internal Error 29] (INFT) 内部错误29 | Internal error 29 (Inverter) 内部错误29(逆变器)
| 165 |  | 177 | [Internal Error 30] (INFU) 内部错误30 | Internal error 30 (Rectifier) 内部错误 30（整流器）
| 166 |  | 179 | [AFE IGBT over-heat error] (TJF2) AFE IGBT 过热故障 | AFE IGBT over-heat error AFE IGBT 过热故障
| 167 |  | 180 | [AFE contactor feedback error] (CRF3) AFE 接触器反馈故障 | AFE contactor feedback error AFE 接触器反馈故障
| 168 |  | 181 | [Pre-settings Transfer Error] (CFI3) 预设置传输错误 | Pre-settings transfer error 预设置传输错误
| 169 |  | 182 | [Circuit Breaker Error] (CBF) 断路器故障 | Circuit breaker error 断路器故障
| 170 |  | 200 | [FDR 1 Error] (FDR1) FDR 1 错误 | FDR Eth embedded error 嵌入式以太网 FDR 错误
| 171 |  | 201 | [FDR 2 Error] (FDR2) FDR 2 错误 | FDR Eth module error以太网模块 FDR 错误
| 172 |  | 208 | [Egy Saving Exit Error] (IDLF) 节能超时 | Idle mode exit error 节能超时
173
174
175
176
177
179
180
181
182
184
185
186
187
188
189
190
191
192
193
194
195
196
197
198
199
200
201
202
203
206
208